## Sheet1
Pagosa Area Water and Sanitation District
100 Lyn Ave. / Pagosa Springs, CO 81147
PHONE: (970) 731-2691
2024 COMMERCIAL WATER METER SIZING WORKSHEET
Date:
Name of Property Owner:
Name of Contact Person:
Name of Business (if applicable):
Property Location
Street Address:
| Subdivision: | [8 empty] | Block: |  |  |  | Lot:
| EACH Type of Fixture |  |  | Number of Fixtures in Bldg 1 | + | Number of Fixtures in Bldg 2 | + | Number of Fixtures in Bldg 3 | = | Total Fixtures | x | *Fixture Unit Multiplier |  |  | = | Total Fixture Unit Value
| Bathub / shower or Combo |  |  |  | + |  | + |  | = | 0 | x | 4 |  |  | = | 0
| Bathroom sink, each set of faucets |  |  |  | + |  | + |  | = | 0 | x | 2 |  |  | = | 0
| Toilet |  |  |  | + |  | + |  | = | 0 | x | 5 |  |  | = | 0
| Urinal |  |  |  | + |  | + |  | = | 0 | x | 3 |  |  | = | 0
| Washing Machine (8 lb) |  |  |  | + |  | + |  | = | 0 | x | 3 |  |  | = | 0
| Washing Machine (15 lb) |  |  |  | + |  | + |  | = | 0 | x | 4 |  |  | = | 0
| Dental unit, cuspidor ** |  |  |  | + |  | + |  | = | 0 | x | 1 |  |  | = | 0
| Clinic Sink** |  |  |  | + |  | + |  | = | 0 | x | 3 |  |  | = | 0
| Bar / Hand Sink** |  |  |  | + |  | + |  | = | 0 | x | 2 |  |  | = | 0
| Drinking Fountain |  |  |  | + |  | + |  | = | 0 | x | 0.25 |  |  | = | 0
| Kitchen sink, hotel or restaurant |  |  |  | + |  | + |  | = | 0 | x | 4 |  |  | = | 0
| Kitchen sink, domestic |  |  |  | + |  | + |  | = | 0 | x | 1.4 |  |  | = | 0
| Dishwasher, domestic |  |  |  | + |  | + |  | = | 0 | x | 1.4 |  |  | = | 0
| Laundry Sink** |  |  |  | + |  | + |  | = | 0 | x | 1.5 |  |  | = | 0
| Service or Mop Basin** |  |  |  | + |  | + |  | = | 0 | x | 3 |  |  | = | 0
| Hose bibb - FIRST** |  |  |  | + |  | + |  | = | 0 | x | 2.5 |  |  | = | 0
| Hose bibb, EACH ADDITIONAL** |  |  |  | + |  | + |  | = | 0 | x | 1 |  |  | = | 0
| Lawn sprinkler, each full head** |  |  |  | + |  | + |  | = | 0 | x | 1 |  |  | = | 0
| Other (Describe) |  |  |  | + |  | + |  | = | 0 | x |  |  |  | = | 0
| Other (Describe) |  |  |  | + |  | + |  | = | 0 | x |  |  |  | = | 0
| * Based on 2015 International Plumbing Code &**2006 Universal Plumbing Code | [10 empty] | 0 | FUY Subtotal |  | : | 0
See Table E103.3(3)
| Fixture Description: |  |  |  |  | GPM: |  |  |  | Number: |  |  | Calculated Fixture Units:
| Fixture Description: |  |  |  |  | GPM: |  |  |  | Number: |  |  | Calculated Fixture Units:
| Fixture Description: |  |  |  |  | GPM: |  |  |  | Number: |  |  | Calculated Fixture Units:
[13 empty] | FUY Total: |  | 0
I affirm that the information given is correct. I acknowledge that the approval given for minimum meter size and maximum water capacity is based solely on the information provided above, and such determination is at the discretion of the Pagosa Area Water and Sanitation District. Any deviation under construction will require resubmission of corrected data for determination of adequacy of meter size.
| Signature (Design Engineer) | [11 empty] | Date Signed
| Signature (Owner/Agent) | [11 empty] | Date Signed
See Page 2 for Instructions
Instructions for completion of the PAWSD Commercial & Multi-Dwelling Water Meter Sizing Worksheet
| Matrix to Determine Meter Size and Water Demand | [7 empty] | Lawn Sprinkler Heads
| Complete the columns of the matrix by supplying the quantity and type of fixtures. Accuracy of the fixture count is necessary to determine the appropriate meter size and Equivalent Units. | [7 empty] | Add all 1/4, 1/2, 3/4, and full irrigation heads to determine the total number of full sprinkler heads. For example, two 1/4 heads and one 1/2 head will equal one full head.
| Commercial Use | [7 empty] | GPM (Gallons per Minute)
| Applies to business, commercial, industrial, and assembly occupancies. Included are the public and common areas in hotels, restaurants, schools, churches, etc. | [8 empty] | When any water requirement is listed by GPM demand, fixture unit count will be determined by using the 2015 International Plumbing Code Table E103.3(3) - Table For Estimating Demand.
Multi-Dwelling Use
May apply to duplex, apartments, condos, townhomes, etc.
Other Water Requirements
There are some process water demands that are not listed, such as car washes. Each of these will be assigned a fixture unit count based upon its GPM demand. Make sure this information is provided.
2024 COMMERCIAL ACCOUNTS
This section to be completedby PAWSD staff.
| Required Service Size and Equivalent Units Chart | [8 empty] | Fixture Count Total (from pg.1): | [5 empty] | 0
| Fixture Unit Count |  | Meter Size | * # Equivalent Units |  |  |  | ** GPM
| 0-30 |  | 3/4" | 1 |  |  |  | 50 |  | Corresponding Meter Size:
| 30.5-52 |  | 1" | 1.5 |  |  |  | 50 | [5 empty] | Acct Current Meter Size:
| 52.5-127 |  | 1" | 2.5 |  |  |  | 50
| 128-375 |  | 1.5" | 5 |  |  |  | 100 | [5 empty] | Corresponding EU:
| 376-700 |  | 2" | 8 |  |  |  | 180 | [5 empty] | Acct Current EU:
| 701-1950 |  | 3" | 16 |  |  |  | 320
| 1951-3700 |  | 4" | 25 |  |  |  | 500
| 3,701-8,200 |  | 6" | 50 |  |  |  | 1000
Meter size/EU ratio determined by hydraulic capacity ratio of meter size as set forth by AWWA Manual M-6.
**With approximate flow of 60 psi at meter
|  | Prepared By: | [7 empty] | Date:
PLEASE NOTE: FEE SCHEDULES ARE SUBJECT TO CHANGE
Appendix E
Table E103.3(3)
Table for Estimating Demand
Supply Systems Predominantly for Flush Tanks
|  |  | Gal per Minute | Water Supply Fixture Units |  | Cubic ft per Minutes |  |  |  | Gal per Minute |  | Water Supply Fixture Units | Cubic ft per Minutes
|  |  | 3 | 1 |  | 0.04104 |  |  |  | 32 |  | 60 | 4.2778
|  |  | 5 | 2 |  | 0.0684 |  |  |  | 35 |  | 70 | 4.6788
|  |  | 6.5 | 3 |  | 0.86892 |  |  |  | 38 |  | 80 | 5.0798
|  |  | 8 | 4 |  | 1.0694 |  |  |  | 41 |  | 90 | 5.4809
|  |  | 9.4 | 5 |  | 1.2659 |  |  |  | 43.5 |  | 100 | 5.8151
|  |  | 10.7 | 6 |  | 1.4304 |  |  |  | 48 |  | 120 | 6.4166
|  |  | 11.8 | 7 |  | 1.5774 |  |  |  | 52.5 |  | 140 | 7.0182
|  |  | 12.8 | 8 |  | 1.7111 |  |  |  | 57 |  | 160 | 7.6198
|  |  | 13.7 | 9 |  | 1.8314 |  |  |  | 61 |  | 180 | 8.1545
|  |  | 14.6 | 10 |  | 1.9517 |  |  |  | 65 |  | 200 | 8.6892
|  |  | 15.4 | 11 |  | 2.0587 |  |  |  | 70 |  | 225 | 9.3576
|  |  | 16 | 12 |  | 2.1389 |  |  |  | 75 |  | 250 | 10.026
|  |  | 16.5 | 13 |  | 2.2057 |  |  |  | 80 |  | 275 | 10.6944
|  |  | 17 | 14 |  | 2.2726 |  |  |  | 85 |  | 300 | 11.3628
|  |  | 17.5 | 15 |  | 2.3394 |  |  |  | 105 |  | 400 | 14.0364
|  |  | 18 | 16 |  | 2.9062 |  |  |  | 124 |  | 500 | 16.5763
|  |  | 18.4 | 17 |  | 2.4597 |  |  |  | 170 |  | 750 | 22.7256
|  |  | 18.8 | 18 |  | 2.5132 |  |  |  | 208 |  | 1000 | 27.8054
|  |  | 19.2 | 19 |  | 2.5667 |  |  |  | 239 |  | 1250 | 31.9495
|  |  | 19.6 | 20 |  | 2.6201 |  |  |  | 269 |  | 1500 | 35.9599
|  |  | 21.5 | 25 |  | 2.8741 |  |  |  | 297 |  | 1750 | 39.703
|  |  | 23.3 | 30 |  | 3.1147 |  |  |  | 325 |  | 2000 | 43.446
|  |  | 24.9 | 35 |  | 3.3286 |  |  |  | 380 |  | 2500 | 50.7984
|  |  | 26.3 | 40 |  | 3.5158 |  |  |  | 433 |  | 3000 | 57.8834
|  |  | 27.7 | 45 |  | 3.7029 |  |  |  | 525 |  | 4000 | 70.182
|  |  | 29.1 | 50 |  | 3.8901 |  |  |  | 593 |  | 5000 | 79.2722